## Instructions
Instructions

## Calculator
| SOLAR TRAINING ACADEMY |  | WWW.SOLARTRAINING.CA
Rooftop PV System |  |  |  |  | Ground Mount PV System
| PLEASE ENTER |  | Comments |  |  | PLEASE ENTER |  | Comments
| Module L (m) | 2 | Length |  |  | Module L (m) | 2 | Length
| Module W (m) | 1 | Width |  |  | Module W (m) | 1 | Width
| Set Back (m) | 2 | 1 - 3 m (Minimum 1 ) |  |  | Set Back (m) | 6 | 3 - 8 m (Minimum 3 from Fence)
| System Size (kW) | 250 | Required in kW |  |  | System Size (kW) | 250 | Required in kW
| Tilt | 5 | Installation Angle |  |  | Tilt | 25 | Installation Angle
| Wattage | 315 | Module Wattage |  |  | Wattage | 315 | Module Wattage
| Sun Altitude Angle | 24 | Shade free operation on 21st Dec (13 for 9AM-3PM) |  |  | Sun Altitude Angle | 24 | Shade free operation on 21st Dec (13 for 9AM-3PM)
| Orientation | 2 | 1= Portrait & 2= Landscape |  |  | Orientation | 2 | 1= Portrait & 2= Landscape
| INTERMEDIATE RESULTS | DO NOT TOUCH / CHANGE |  |  |  | INTERMEDIATE RESULTS | DO NOT TOUCH / CHANGE
|  | 2 | Orientation Selected |  |  |  | 2 | Orientation Selected
|  | 0.1745 | Module Height @ Chosen tilt |  |  |  | 0.87249 | Module Height @ Chosen tilt
|  | 0.39193 | Inter-row-distance @ Tilt and Sun Altitude Angle |  |  |  | 1.9596 | Inter row distance @ Tilt and Sun Altitude Angle
|  | 0 | Additional Inter-row-distance for O&M |  |  |  | 1.0404 | Additional Inter-row-distance for O&M
|  | 2.3843 | Area Required Per Module |  |  |  | 4.7997 | Area Required Per Module
|  | 794 | Approximate Modules required |  |  |  | 794 | Approximate Modules required
|  | 1894 | Area Required for Total # of Modules |  |  |  | 3811 | Area Required for Total # of Modules
|  | 348.1609 | Setback area required |  |  |  | 1481.5991 | Setback area required
| FINAL RESULTS |  |  |  |  | FINAL RESULTS
| Required Roof Area | 2242.1609 | square meter |  |  | Required Roof Area | 5292.5991 | square meter
|  | 7354.2877 | squre feet |  |  |  | 1.3078 | acres
| Notes: |  |  |  |  | Notes:
1 | Following would be added to (if apply) to have realistic estimation |  |  |  | 1 | Following would be added to (if apply) to have realistic estimation
| Equip. Area | 0 | Estimate & input roof area occupied to HVAC & other equip |  |  | Municplility Required Setback | 0 | 20 - 100 m
| Equip. Area Shade | 0 | Estimate & input area shaded by HVAC, etc. |  |  | Water body etc. | 0 | 30 - 100 m
| Inverter(s) Area | 0 | Area required to install inverter(s) on the roof |  |  | E - House | 0 | Area to install Transformer, Discoonects, etc.
| Total Area Required | 2242.1609 | square meter |  |  | Total Area Required | 5292.5991 | square meter
|  | 7354.2877 | squre feet |  |  |  | 1.3078 | acres
2 | Flat Roof only |  |  |  | 2 | Ground Mount only
3 | Additional or different considerations may be required |  | 4 | Landscape & Portrait orientations result approximately same sizes |  | Additional or different considerations may be required
4 | Landscape & Portrait orientations result approximately same sizes |  | 5 | Site may favor one orientation over the other |  | Landscape & Portrait orientations result approximately same sizes
5 | Site may favor one orientation over the other |  |  |  | 5 | Site may favor one orientation over the other
| Disclaimer: |  |  |  |  | Disclaimer:
| For educational purpose only. |  |  |  |  | For educational purpose only.